{"text_format":"3","workbook":"xls","n_sheets":3,"sheets":["Sheet1","Sheet2","Sheet3"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet1","index":0,"n_rows":52,"n_cols":14,"rows_kept":52,"merged":[[0,0,0,13],[1,0,1,13],[2,0,4,0],[2,1,4,1],[2,2,4,2],[2,3,4,3],[2,12,4,12],[2,13,4,13]],"flags":["formulas_cached_only"]}
["12上半月管网水半月检常规项目检验汇总表"]
["委托单位名称：淄博市自来水有限责任公司                                                                               检测单位：淄博安瑞水质检测有限责任公司                                                                                                                                                                                                                                                                                               "]
["序号","采样日期","采样地点","样品编号","菌落总数","总大肠菌群","色度","浑浊度","臭和味","肉眼可见物","二氧化氯","高锰酸盐指数（以O2计）","报告日期","检测人员"]
[{"$nulls":4},"CFU/mL","CFU/100mL","度","NTU","/","/","mg/L","mg/L"]
[{"$nulls":4},"≤100","不应检出","≤15","≤1","无异臭、异味","无","出厂水和末梢水中限值0.8，出厂水中余量≥0.1，末梢水中余量 ≥0.02","≤3"]
[1,"2025.12.01","新村西路140号原市水资办","20251201-1013",5,"未检出","<5",{"v":0.3,"d":"0.30"},"无","无",0.03,"/","2025.12.03"," 王晓芳"]
[2,"2025.12.01","淄博市政务中心","20251201-1014",3,"未检出","<5",{"v":0.2,"d":"0.20"},"无","无",0.04,"/","2025.12.03"," 王晓芳"]
[3,"2025.12.01","张店区疾控中心","20251201-1015","未检出","未检出","<5",0.26,"无","无",0.04,"/","2025.12.03"," 王晓芳"]
[4,"2025.12.01","西苑社区","20251201-1016",13,"未检出","<5",0.26,"无","无",0.03,"/","2025.12.03"," 王晓芳"]
[5,"2025.12.01","五公里党群站","20251201-1017",10,"未检出","<5",0.21,"无","无",0.05,1.37,"2025.12.03"," 王晓芳"]
[6,"2025.12.01","   市自来水公司南定营销服务中心","20251201-1018",3,"未检出","<5",0.32,"无","无",0.04,1.25,"2025.12.03"," 王晓芳"]
[7,"2025.12.01","市自来水公司铝城营业所","20251201-1019",16,"未检出","<5",0.37,"无","无",0.03,"/","2025.12.03"," 王晓芳"]
[8,"2025.12.01","经开区后南定村卫生室","20251201-1020",7,"未检出","<5",0.25,"无","无",0.03,"/","2025.12.03"," 王晓芳"]
[9,"2025.12.01","张南路101号中石油加油站","20251201-1021",2,"未检出","<5",0.23,"无","无",0.04,"/","2025.12.03"," 王晓芳"]
[10,"2025.12.01","山泉路启星比亚迪4S店","20251201-1022",2,"未检出","<5",0.21,"无","无",0.05,"/","2025.12.03"," 王晓芳"]
[11,"2025.12.08","天勤苑社区","20251208-1023",11,"未检出","<5",{"v":0.3,"d":"0.30"},"无","无",0.04,1.61,"2025.12.10"," 王晓芳"]
[12,"2025.12.08","高新区金晶大道汇驰奔驰4S店","20251208-1024",2,"未检出","<5",0.22,"无","无",0.03,"/","2025.12.10"," 王晓芳"]
[13,"2025.12.08","金都花园社区","20251208-1025",5,"未检出","<5",0.24,"无","无",0.04,1.77,"2025.12.10"," 王晓芳"]
[14,"2025.12.08","星悦城社区","20251208-1026",2,"未检出","<5",0.22,"无","无",0.04,1.71,"2025.12.10"," 王晓芳"]
[15,"2025.12.08","外商居住区","20251208-1027",7,"未检出","<5",0.26,"无","无",0.04,"/","2025.12.10"," 王晓芳"]
[16,"2025.12.08","市自来水开发区营业所","20251208-1028","未检出","未检出","<5",{"v":0.2,"d":"0.20"},"无","无",0.05,"/","2025.12.10"," 王晓芳"]
[17,"2025.12.08","淄博市十一中","20251208-1029",7,"未检出","<5",0.21,"无","无",0.03,"/","2025.12.10"," 王晓芳"]
[18,"2025.12.08","丽莎会议中心","20251208-1030",10,"未检出","<5",0.24,"无","无",0.03,"/","2025.12.10"," 王晓芳"]
[19,"2025.12.08","华侨城警务室","20251208-1031",13,"未检出","<5",0.33,"无","无",0.04,"/","2025.12.10"," 王晓芳"]
[20,"2025.12.09","淄博市委","20251209-1032",7,"未检出","<5",0.33,"无","无",0.05,"/","2025.12.11"," 王晓芳"]
[21,"2025.12.09","张店区军休所","20251209-1033",11,"未检出","<5",0.32,"无","无",0.04,"/","2025.12.11"," 王晓芳"]
[22,"2025.12.09","五里桥生活区","20251209-1034",3,"未检出","<5",0.24,"无","无",0.03,"/","2025.12.11"," 王晓芳"]
[23,"2025.12.09","祥瑞花园社区","20251209-1035",21,"未检出","<5",0.31,"无","无",0.04,"/","2025.12.11"," 王晓芳"]
[24,"2025.12.09","张店八中","20251209-1036",10,"未检出","<5",0.24,"无","无",0.04,"/","2025.12.11"," 王晓芳"]
[25,"2025.12.09","淄博市图书馆","20251209-1037",2,"未检出","<5",0.25,"无","无",0.03,"/","2025.12.11"," 王晓芳"]
[26,"2025.12.09","积家村党群服务中心","20251209-1038","未检出","未检出","<5",0.32,"无","无",0.04,1.68,"2025.12.11"," 王晓芳"]
[27,"2025.12.09","明德苑社区","20251209-1039",1,"未检出","<5",{"v":0.2,"d":"0.20"},"无","无",0.03,"/","2025.12.11"," 王晓芳"]
[28,"2025.12.10","恒嘉园社区","20251210-1040",10,"未检出","<5",0.32,"无","无",0.04,"/","2025.12.12"," 王晓芳"]
[29,"2025.12.10","人民东路小学","20251210-1041",3,"未检出","<5",0.25,"无","无",0.05,"/","2025.12.12"," 王晓芳"]
[30,"2025.12.10","张店区保安公司","20251210-1042",5,"未检出","<5",0.24,"无","无",0.03,"/","2025.12.12"," 王晓芳"]
[31,"2025.12.10","润德实业公司","20251210-1043",1,"未检出","<5",0.22,"无","无",0.05,"/","2025.12.12"," 王晓芳"]
[32,"2025.12.10","行政执法局湖田中队","20251210-1044",2,"未检出","<5",0.33,"无","无",0.04,"/","2025.12.12"," 王晓芳"]
[33,"2025.12.10","淄博市公交东站","20251210-1045",1,"未检出","<5",0.25,"无","无",0.03,"/","2025.12.12"," 王晓芳"]
[34,"2025.12.10","洪三社区","20251210-1046",9,"未检出","<5",0.35,"无","无",0.04,1.65,"2025.12.12"," 王晓芳"]
[35,"2025.12.11","淄博市工商局","20251211-1047",7,"未检出","<5",0.23,"无","无",0.05,"/","2025.12.13"," 王晓芳"]
[36,"2025.12.11","市自来水公司新区营业所","20251211-1048",3,"未检出","<5",0.24,"无","无",0.05,"/","2025.12.13"," 王晓芳"]
[37,"2025.12.11","颐臻园社区","20251211-1049",5,"未检出","<5",0.31,"无","无",0.03,"/","2025.12.13"," 王晓芳"]
[38,"2025.12.11","世纪花园社区","20251211-1050",11,"未检出","<5",0.33,"无","无",0.03,"/","2025.12.13"," 王晓芳"]
[39,"2025.12.11","瑞丰苑社区","20251211-1051",4,"未检出","<5",0.27,"无","无",0.04,{"v":1.7,"d":"1.70"},"2025.12.13"," 王晓芳"]
[40,"2025.12.11","科技苑物业","20251211-1052",6,"未检出","<5",{"v":0.2,"d":"0.20"},"无","无",0.03,"/","2025.12.13"," 王晓芳"]
[41,"2025.12.15","淄博市体育馆","20251215-1053",8,"未检出","<5",0.23,"无","无",0.04,"/","2025.12.17"," 王晓芳"]
[42,"2025.12.15","福源汇社区","20251215-1054",5,"未检出","<5",0.22,"无","无",0.05,"/","2025.12.17"," 王晓芳"]
[43,"2025.12.15","孝妇河湿地公园喷泉广场","20251215-1055",2,"未检出","<5",{"v":0.3,"d":"0.30"},"无","无",0.03,1.38,"2025.12.17"," 王晓芳"]
[44,"2025.12.15","石家社区","20251215-1056",12,"未检出","<5",0.24,"无","无",0.04,1.64,"2025.12.17"," 王晓芳"]
[45,"2025.12.15","盛世康城社区","20251215-1057",7,"未检出","<5",0.21,"无","无",0.03,"/","2025.12.17"," 王晓芳"]
[46,"2025.12.15","福瑞家园社区","20251215-1058",1,"未检出","<5",0.19,"无","无",0.04,{"v":1.9,"d":"1.90"},"2025.12.17"," 王晓芳"]
[null,null,"以下空白"]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}